## Cover
SEDIBENG TVET COLLEGE - VANDERBILJPARK CAMPUS
BILL OF QUANTITIES
(PRICED)

## 1 - Back Up Power
SUPPLY AND INSTALLATION OF THE BACKUP GENERATORS AT VANDERBIJLPARK CAMPUS, SEDIBENG COLLEGE.
DESCRIPTION | UNIT | QUANTITY | RATE | AMOUNT
SECTION NO. 1
PRELIMINARIES AND GENERAL
BILL NO. 1
FIXED CHARGE ITEMS
Contractual requirements.
Insurances | SUM | 1
Programming | SUM | 1
Performance Security | SUM | 1
Retention Guarantee | SUM | 1
Establishment of Facilities on the Site
Facilities for Engineer
Equipment for the Engineer's Staff | SUM | 1
Facilities for Contractor | H4
Offices and Storage Sheds | SUM | 1
Workshops | SUM | 1
Site Establishment | SUM | 1
Living Accomodation - The Contractor to supply a breakdown of | SUM | 1
the different categories namley: Supervision, Skilled Labor,
Semi Skilled Labour and Unskilled Labour
Laboratory Facilities | SUM | 1
Ablution and Latrine Facilities | SUM | 1
Tools and Equipment | SUM | 1
Water Supplies | SUM | 1
Electric Power | SUM | 1
Communication | SUM | 1
Air Supplies | SUM | 1
Dealing with Water | SUM | 1
Access | SUM | 1
Facilities Requiring Special Attention
Security | SUM | 1
Safety | SUM | 1
Samples and certification of materials | SUM | 1
Testing Authority | SUM | 1
Other Contractors | SUM | 1
Quality Assurance | SUM | 1
Orders and Indents | SUM | 1
Site Meetings | SUM | 1
Plant for the Works | SUM | 1
Transport on the site | SUM | 1
Transport of the Workforce to and from the site | SUM | 1
Supervision for the duration of the construction | SUM | 1
Company and head office overheads costs for the duration of | SUM | 1
the contract works
Other fixed charge obligation - Contractor to submit details | SUM | 1
Remove site establishment on completion | SUM | 1
VALUE RELATED ITEMS
Contractual requirements.
Insurances | SUM | 1
Programming | SUM | 1
Performance Security | SUM | 1
Retention Guarantee | SUM | 1
Establishment of Facilities on the Site
Facilities for Engineer
Equipment for the Engineer's Staff | SUM | 1
Facilities for Contractor
Offices and Storage Sheds | SUM | 1
Workshops | SUM | 1
Site Establishment | SUM | 1
Living Accomodation - The Contractor to supply a breakdown of | SUM | 1
the different categories namley: Supervision, Skilled Labor,
Semi Skilled Labour and Unskilled Labour
Laboratory Facilities | SUM | 1
Ablution and Latrine Facilities | SUM | 1
Tools and Equipment | SUM | 1
Water Supplies | SUM | 1
Electric Power | SUM | 1
Communication | SUM | 1
Air Supplies | SUM | 1
Dealing with Water | SUM | 1
Access | SUM | 1
Facilities Requiring Special Attention
Security | SUM | 1
Safety | SUM | 1
Samples and certification of materials | SUM | 1
Testing Authority | SUM | 1
Other Contractors | SUM | 1
Quality Assurance | SUM | 1
Orders and Indents | SUM | 1
Site Meetings | SUM | 1
Plant for the Works | SUM | 1
Transport on the site | SUM | 1
Transport of the Workforce to and from the site | SUM | 1
Supervision for the duration of the construction | SUM | 1
Company and head office overheads costs for the duration of | SUM | 1
the contract works
Other value related obligations - Contractor to submit details | SUM | 1
Remove site establishment on completion | SUM | 1
TIME RELATED ITEMS
Contractual requirements.
Insurances | SUM | 1
Programming | SUM | 1
Performance Security | SUM | 1
Retention Guarantee | SUM | 1
Establishment of Facilities on the Site
Facilities for Engineer
Equipment for the Engineer's Staff | SUM | 1
Facilities for Contractor
Offices and Storage Sheds | SUM | 1
Workshops | SUM | 1
Site Establishment | SUM | 1
Living Accomodation - The Contractor to supply a breakdown of | SUM | 1
the different categories namley: Supervision, Skilled Labor,
Semi Skilled Labour and Unskilled Labour
Laboratory Facilities | SUM | 1
Ablution and Latrine Facilities | SUM | 1
Tools and Equipment | SUM | 1
Water Supplies | SUM | 1
Electric Power | SUM | 1
Communication | SUM | 1
Air Supplies | SUM | 1
Dealing with Water | SUM | 1
Access | SUM | 1
Facilities Requiring Special Attention
Security | SUM | 1
Safety | SUM | 1
Samples and certification of materials | SUM | 1
Testing Authority | SUM | 1
Other Contractors | SUM | 1
Quality Assurance | SUM | 1
Orders and Indents | SUM | 1
Site Meetings | SUM | 1
Plant for the Works | SUM | 1
Transport on the site | SUM | 1
Transport of the Workforce to and from the site | SUM | 1
Supervision for the duration of the construction | SUM | 1
Company and head office overheads costs for the duration of | SUM | 1
the contract works
Other time related obligation - Contractor to submit details | SUM | 1
Remove site establishment on completion | SUM | 1
TOTAL - SECTION 1 - BILL NO.1 - PRELIMINARIES AND GENERAL
SECTION NO. 2
GENERATORS
BILL NO. 1
DISTRIBUTION KIOSKS
Electrical distribution switchboards as specified and as per the single line diagrams complete with pad lockable doors, frames, sub-frames, chassis, fixtures, fittings, with spare space, including all switching equipment.
(a) Weather proof distribution kiosk for C block - as per SLD to be issued | each | 1
(b) Strip existing circuit breakers and install a new ones | each | 1
(d) DB Plinth | each | 1
Circuit Breakers
Circuit breakers to be Schneider, ABB, CBI or Hager
(a) new 600A CB 25KA, inside minisub | each | 1
(b) new 600A CB 25KA, inside Main Kiosk (B- Block) | each | 1
(b) new 200A CB 25KA, inside Main BD - L Block | each | 1
LOW VOLTAGE DISTRIBUTION
Supply, deliver, install and terminate Cu PVC SWA PVC 600/1000V Cable, in trenches, sleeves or on cable trays
95mm² PVC/SWA/PVC/PVC 4 core (From main Supply to Generator)
Supply and delivery | Meter | 60
Installation | Meter | 60
95mm² PVC/SWA/PVC/PVC 4 core (From Generator to Main Breaker in a minisub)
Supply and delivery | Meter | 60
Installation | Meter | 60
50mm² PVC/SWA/PVC/PVC 4 core [From Main Kiosk (B- Block) to Main BD - C Block]
Supply and delivery | Meter | 80
Installation | Meter | 80
120mm² PVC/SWA/PVC/PVC 4 core [From Main Kiosk (B- Block) to Main BD - L Block]
Supply and delivery | Meter | 200
Installation | Meter | 200
185mm² PVC/SWA/PVC/PVC 4 core [From Main supply to Main BD - Main Kiosk B- Block]
Supply and delivery | Meter | 150
Installation | Meter | 120
Bare Stranded Copper Earth Wire Terminations
Stranded copper earth wire terminations for insulated/bare conductor complete, including drilling, bolting, lugs, connections and terminating.
25mm2 CU | Each | 2
50mm2 CU | Each | 6
70mm2 CU | Each | 8
Bare Stranded Copper Earth Wire
Bare stranded copper earth wire strapped to cables, terminations are measured elsewhere.
25mm2 CU | meters | 80
50mm2 CU | meters | 120
70mm2 CU | meters | 200
Low Voltage Cable Terminations
Cable terminations complete glands, shrouds, lugs, connections and commissioning.
120mm2 PVC/SWA/PVC/PVC 4 Core CU From Main Kiosk (B- Block) to Main BD - L Block | Each | 8
95mm² PVC/SWA/PVC/PVC 4 core (From main Supply to Generator) | Each | 8
95mm² PVC/SWA/PVC/PVC 4 core (From Generator to Main Breaker in a minisub) | Each | 8
50mm² PVC/SWA/PVC/PVC 4 core [From Main Kiosk (B- Block) to Main BD - C Block] | Each | 8
120mm² PVC/SWA/PVC/PVC 4 core [From Main Kiosk (B- Block) to Main BD - L Block] | Each | 8
185mm² PVC/SWA/PVC/PVC 4 core [From Main Kiosk (B- Block) to Main BD - L Block] | Each | 8
Cable Trenches
Excavate for cable and sleeve trench including temporary support of sides, keeping excavations dry, backfilling and compacting to the engineers specification including bedding under and filling around cable comprising sifted sand
Soil- Dig up Existing Cables | m3 | 470
Soil- New Trenches to and from Mini-sub, generator, and new DB | m3 | 470
GENERATOR INSTALLATION
Supply, delivery, Test, install and commission of standby power
Supply, Deliver and install 200kVA generator with sound proof canopy
Supply and delivery | Sum | 1
Installation (including plinth and fencing) | Sum | 1
Supply, Deliver and install sound proof canopy for the existing 500kVA generator
Supply and delivery | Sum | 1
Installation | Sum | 1
MAINTENANCE TO THE BACKUP GENERATOR
36 months maintenance of the generator installation and it's ancillaries as per ''Manufacturers Guidelines" | each | 1
Generator call-out fee per hour | each | 36
Diesel delivery by bowser inclusive of: 630 litres of diesel and 2 refills a month | each | 36
Generator Reporting
(a) Deepsea gateway 890 | each | 1
(b ) Router | each | 1
(c ) Sim including airtime and data for remote monitoring for 36 months | each | 1
(d ) System Setup | each | 1
(e ) Installation of gateway on existing generator | each | 1
GENERAL
STRIPPING OF EXISTING ELECTRICAL INSTALLATION
Allow for the stripping of existing electrical installation | Sum | 1
AS BUILT DOCUMENTATION
Allow for the mark up of record drawings, submission of 3 sets of as-built files containing material specifications, DB workshop drawings, COC's, IR scanning report, etc. Files to comply with the Electrical Engineer's specification and requirements. | Sum | 1
INSPECTION, TESTING AND COMMISSIONING
Inspection, testing and handing over of the complete installation in the presence of Engineer and certify the results on the Certificate of compliances by an accredited (Master Installation Electrician). | Sum | 1
LABELLING
Lable all circuits and install signage to the panels | sum | 1
TOTAL - SECTION 2 - BILL NO.1 - GENERATORS
SECTION NO.3
RENOVATIONS & REFURBISHMENTS
BILL NO. 1
CONTINGENCIES
Allow 10% for Contingencies re any unforeseen work, contingencies to be used at the discretion of the client through the principal agent. | Item | 1
TOTAL- SECTION 3 - BILL NO. 1 - CONTINGENCIES
TOTAL EXCLUDING VAT
VAT @ 15%
TOTAL INCLUDING VAT